## Sheet1
GRUNDFOS BOOSTER SIZING PROGRAM
INSTRUCTIONS: YOU SHOULD ONLY ENTER DATA IN YELLOW AREAS | BLUE AREAS ARE CALCULATED DATA
STEP - 1
FIXTURE COUNT AND ASSIGNMENT OF FIXTURE UNITS
FIXTURE TYPE | QTY. | FIXTURE UNITS | TOTAL |  | FIXTURE UNITS | GPM
water closet, public w/flush valve |  | 10 | 0 |  | 75 | 35
water closet, public w/flush tank |  | 5 | 0 |  | 125 | 50
wall urinal, public, 3/4" flush valve |  | 5 | 0 |  | 250 | 75
lavatory, public |  | 2 | 0 |  | 300 | 85
shower head, public, mixing valve |  | 4 | 0 |  | 400 | 100
service sink |  | 3 | 0 |  | 500 | 125
kitchen sink, commercial |  | 4 | 0 |  | 750 | 175
washing machine, 15#, commercial |  | 4 | 0 |  | 1000 | 210
water closet, private w/flush valve |  | 6 | 0 |  | 1500 | 265
water closet, private w/flush tank |  | 2.2 | 0 |  | 2000 | 320
lavatory, private |  | 0.7 | 0 |  | 2500 | 375
bathtub, private |  | 1.4 | 0 |  | 3000 | 430
kitchen sink, private |  | 1.4 | 0 |  | 4000 | 570
dishwasher, private, automatic |  | 1.4 | 0 |  | 5000 | 665
washing machine, 8#, private |  | 1.4 | 0 |  | 6000 | 780
1/2" hose bib |  | 4 | 0 |  | 7000 | 875
3/4" hose bib |  | 6 | 0 |  | 8000 | 960
1" hose bib |  | 10 | 0
other fixtures |  |  | 0
other fixtures |  |  | 0
other fixtures |  |  | 0
YOUR TOTAL FIXTURE UNITS |  |  | 0
STEP - 2
FIXTURE UNIT TO FLOW CONVERSION
YOUR TOTAL FIXTURE UNITS | YOUR SYSTEM FLOW REQUIRED
0 | 35
STEP - 3
YOUR PRESSURE BOOST CALCULATION |  |  | FEET | PSI
STATIC PRESSURE - (ELEVATION TO HIGHEST FIXTURE) |  |  |  | 0
SYSTEM FRICTION LOSSES "ESTIMATED" = (STATIC PRESSURE X.10) |  |  |  | 0
PRESSURE REQUIRED AT FARTHEST FIXTURE - (TYPICAL 35PSI) |  |  |  | 35
REQUIRED SYSTEM PRESSURE (ADD ROWS 1-3) |  |  |  | 35
MINIMUM SUCTION PRESSURE (LOWEST PRESSURE SUPPLIED THE SUCTION SIDE OF SYSTEM)
YOUR TOTAL REQUIRED SYSTEM BOOST |  |  |  | 35
STEP - 4
YOUR BUILDING/SYSTEM FLOW AND HEAD REQUIRED
GPM @ | PSI |  | or FEET OF HEAD
35 | 35 |  | 80.85
STEP - 5
YOUR SYSTEM DESIGN
NUMBER OF PUMPS | EACH PUMP LOAD PERCENTAGE |  | INDIVIDUAL PUMP FLOW REQUIREMENTS
0
STEP - 6
SIZE EACH OF YOUR SYSTEM PUMPS BASED ON DATA BELOW
GPM @ | PSI |  | or FEET OF HEAD
0 | 35 |  | 80.85
STEP - 7 (REQUIRED EXPANSION TANK)
PUMP TYPE | GAL. REQ.
CR or CRE-3 | 4.4
CR or CRE-5 | 4.4
CR or CRE-10 | 10.2
CR or CRE-15 | 34
CR or CRE-20 | 34
CR or CRE-32 | 44
CR or CRE-45 | 86
CR or CRE-64 | 132
CR or CRE-90 | 132
*INDIVIDUAL PUMP CURVES FOR THE PUMPS CAN BE FOUND IN THE GRUNDFOS BOOSTERPAQ HYDRO MPC PRODUCT GUIDE
YOU NEED A:
0 | PUMP SYSTEM
CAPABLE OF | 0 | GPM PER PUMP AT
80.85 | FEET OF HEAD.
TOTAL SYSTEM GPM | 35
TOTAL SYSTEM FEET OF HEAD | 80.85
VOLTAGES AVAILABLE
MAIN WATER LINE SIZE
IF YOU'D LIKE US TO REVIEW YOUR INFORMATION, PLEASE FILL IN THE SECTION BELOW, SELECT "FILE" "PRINT" "PRINT", AND THEN SEND YOUR PRINTOUT TO CUSTOMERSERVICE@WMSSALES.COM
*** FOR ASSISTANCE, CONTACT US AT 716-741-9575 (Ext. 3)
YOUR NAME: |  | E-MAIL:
COMPANY NAME: |  | PHONE:
ADDRESS:
CITY, STATE, ZIP CODE:
COMMENTS/QUESTIONS: